## 110VDC batteries
SCHEDULE OF TECHNICAL INFORMATION
110 V D.C. Supply
Item | Particulars | Unit | Employer's Requirement | Contractor's Value
1 | Batteries (to be filled in for each type of battery
1.1 | Type |  | Hoppecke GridPower VM2 OSP.HC
1.2 | Type of cells |  | Vented Lead-acid Battery
1.3 | Required Standby Time (Hrs) | Hrs | 12
1.4 | Supported Emergency light Time (Hrs) | Hrs | 4
1.5 | Ambient Temperature: Min / Maximum | Deg C | 5 to 40 Deg C
1.6 | Ambient Temperature: Typical | Deg C | 20 to 35 Deg C
2 | Capacity / Load Requirements
2.1 | Maximum discharge current (1 min) | A | 327
2.2 | Total Battery Uncorrected Capacity (Ah) | Ah | 552
2.3 | Temperature Correction Factor (considering typical temperature range) |  | 1.08
2.4 | Ageing Factor |  | 1.25
2.5 | Design margin |  | 1.1
2.6 | Total Corrected Ah required | Ah | 1390 Ah
2.7 | K rating of battery |  | 1.1 - 1.15
Note: Supplier to confirm the battery capacity calculation and consider the impact of the Capacity Rating of the battery for the max Discharge Current specified over 1 min period.
3 | Voltage Requirements
3.1 | Nominal DC System Voltage (V) | V | 110
3.2 | System Float Voltage (+10%) | V | 121
3.3 | End-of-discharge System Voltage (-10%) | V | 99
3.4 | Cell Float Voltage (V/cell) | V | 2.23
3.5 | Number of cells |  | 52
4 | General Requirements
4.1 | Max. charging current | A
4.2 | Recommended Charger capacity | A
4.3 | Floating charging current | A
4.4 | Floating charging voltage | V
4.5 | Acid density of fully charged battery | °BE
4.6 | Water consumption per cell per year | cm3
4.7 | Internal resistance per cell | ohm
4.8 | Internal resistance of the complete battery | ohm
4.9 | Max. permissible ambient air temperature | °C
4.10 | Material of the cell containers
4.11 | Material of the battery terminals
4.12 | Type of connection between the cells
4.13 | Weight per cell including acid | kg
5 | Bases |  | Included in scope of supply
5.1 | Bases (dual row) |  | Wooden
5.2 | Weigh of the complete battery including acid and bases | kg
5.3 | Overall dimension of the complete battery including the bases
| - length | mm
| - height | mm
| - width | mm

## 48VDC batteries
SCHEDULE OF TECHNICAL INFORMATION
48 V D.C. Supply
Item | Particulars | Unit | Employer's Requirement | Contractor's Value
1 | Batteries (to be filled in for each type of battery
1.1 | Type |  | Hoppecke GridPower VM2 OSP.HC
1.2 | Type of cells |  | Vented Lead-acid Battery
1.3 | Required Standby Time (Hrs) | Hrs | 12
1.4 | Supported Emergency light Time (Hrs) | Hrs | NA
1.5 | Ambient Temperature: Min / Maximum | Deg C | 5 to 40 Deg C
1.6 | Ambient Temperature: Typical | Deg C | 20 to 35 Deg C
2 | Capacity / Load Requirements
2.1 | Maximum discharge current (1 min) | A | 25
2.2 | Total Battery Uncorrected Capacity (Ah) | Ah | 300
2.3 | Temperature Correction Factor (considering typical temperature range)
2.4 | Ageing Factor |  | 1.25
2.5 | Design margin |  | 1.2
2.6 | Total Corrected Ah required | Ah | 608 Ah
Note: Supplier to calculate the correct battery capacity and consider the impact of the Capacity Rating of the battery for the max Discharge Current specified over 1 min period.
3 | Voltage Requirements
3.1 | Nominal DC System Voltage (V) | V | 48
3.2 | System Float Voltage (+10%) | V | 52.8
3.3 | End-of-discharge System Voltage (-10%) | V | 43.2
3.4 | Cell Float Voltage (V/cell) | V | 2.23
3.5 | Number of cells |  | 24
4 | General Requirements
4.1 | Max. charging current | A
4.2 | Recommended Charger capacity | A
4.3 | Floating charging current | A
4.4 | Floating charging voltage | V
4.5 | Acid density of fully charged battery | °BE
4.6 | Water consumption per cell per year | cm3
4.7 | Internal resistance per cell | ohm
4.8 | Internal resistance of the complete battery | ohm
4.9 | Max. permissible ambient air temperature | °C
4.10 | Material of the cell containers
4.11 | Material of the battery terminals
4.12 | Type of connection between the cells
4.13 | Weight per cell including acid | kg
5 | Bases |  | Included in scope of supply
5.1 | Bases (dual row) |  | Wooden
5.2 | Weigh of the complete battery including acid and bases | kg
5.3 | Overall dimension of the complete battery including the bases
| - length | mm
| - height | mm
| - width | mm