Head Office

Av. 25 de Setembro, 420

Prédio JAT- 40  - N3

Maputo Moçambique

Tel: +258(21) 313427

Fax: +258(21) 313447

CAMDEN EDWALENI LINE

- Earth Wire Damaged: Tower span 150 -151 – right Side.

Scope:

- Inspect and confirm extend of damaged on the earth wire.

- Repair damage section using an approved preformed wrap.

- Conductor anomaly discoloured: Tower span from 157 – 159.

Scope:

- Assess and report whether discoloration is due to overheating, corrosion, or surface contamination.

- If applicable, propose corrective measures.

- Spacer missing on Tower 46, On the Edwaleni Side.

Scope:

- Inspect and identify the required spacer.

- Supply and Install spacer damper as per line specifications.

- Bird Nest on Tower 98, 99, 241, 243,261,296 and 297.

Scope:

- Carry out Inspection and removal of active/inactive nest (in accordance with environmental regulations

- Supply and Install bird guards/diverters on affected towers to prevent recurrence as per NTCSA specifications.

EDWALENI MAPUTO LINE

- Insulator pulling: Tower 66 and 115.

Scope:

- Conduct close inspection of insulator strings at towers to confirm degree of “pulling”.

- Check associated hardware for deformation of looseness.

- Assess integrity of insulators, towers, fittings and report integrity and the need of further action to restore correct specification. If any action as re-align or tighten insulator strings, fittings need/be possible to do while contractor on site, contractor must report to client before contractor leave site.

- Tower label broken: Tower 113.

Scope:

- Remove broken tower identification plate.

- Supply and install a new tower label as per standard specifications.

- Earth Wire Jumper broken: Tower 145, 169,170 and 179.

Scope:

- Inspect the earth wire jumper connections at the affected towers.

- Remove damaged jumpers and associated fittings.

- Supply and install new earth wire jumpers of the correct size and type, with proper compression fittings.